## STAIR CASE (IMPERIAL)
DOCUMENT : STAIR CASE PRESSURIZATION CALCULATION
| Total No. of Floors | = | 6
| Door Width | = | 2.97 | ft
| Door Height | = | 6.93 | ft
| Door Perimeter | = | 19.8 | ft
| Crack | = | 0.2 | in | = | 0.01666 | ft
| Leakage Area per Door | = | 0.32987 | ft2
| Total Leakage Area, (ALEAKAGE) | = | 1.9792 | ft2
1. Air Volume require when all doors are closed :
| Q1 | = | 2610 | x | ALEAK | x | P1/n
| Q1 | = | Volume of Air Required (CFM)
| ALEAKAGE | = | Leakage Area (ft2) |  |  | 1.9792 | ft2
| P | = | Diferential Pressure |  |  | 0.06 | inw
| n | = | Leakage Factor |  |  | 2
| Q1 | = | 1265.341 | cfm
Although the effective leakage area is known, there are other leaks we are not aware of,
To account for these leaks, Q is increased by 50%, hence:
| Q1 | = | 1898.0115 | cfm
2. Air volume required when doors are opened :
| Door Area | = | 20.5821 | ft2
| Velocity across Door | = | 196 | fps
| No. of Door Open considered | = | 3
| Q2 | = | Velocity across door x Door Area x No. of Door Open
| Q2 | = | 12102.2748 | cfm
3. Total Air Supplied by the fan :
| Q | = | Q1 + Q2
| Q | = | 14000.2863 | CFM
| at 1500 fpm | → | f = | 0.1 | "/100 ft
| Duct Length | = | 120 | ft
| Friction Loss through duct | = | (Duct Length x 1.25 x f)
| Friction Loss | = | 0.15 | "
| Total Static Pressure | = | (PD at Register + Friction Loss + Volume Damper)*30%
|  | = | 0.2 | + | 0.15 | + | 0.2
|  | = | 0.715 | "
| Total Static Pressure on Fan | = | 0.715 | + | 0.06
| Total Fan Static Pressure | = | 0.775 | "
4. Relief Damper Sizing :
| Air to be releived, Q2 | = | 12102.2748 | cfm
| Area of Pressure Relief, A | = | 12102.2748
|  |  | 2610 | x | 0.06
| A | = | 18.93 | ft2
½

## STAIR CASE(SI)
DOCUMENT : STAIR CASE PRESSURIZATION CALCULATION
DATE : | 2020-01-18
| Total No. of Floors | = | 6
| Door Width | = | 0.9 | m | = | 2.952 | ft
| Door Height | = | 2.1 | m | = | 6.888 | ft
| Door Perimeter | = | 6 | m
| Crack | = | 5 | mm | = | 0.005 | m
| Leakage Area per Door | = | 0.03 | m2
| Total Leakage Area, (ALEAKAGE) | = | 0.18 | m2
1. Air Volume require when all doors are closed :
| Q1 | = | 0.827 | x | ALEAK | x | P1/n
| Q1 | = | Volume of Air Required (m3)
| ALEAKAGE | = | Leakage Area (m2) |  |  | 0.18 | m2
| P | = | Diferential Pressure |  |  | 15 | Pa
| n | = | Leakage Factor |  |  | 2
| Q1 | = | 0.57653 | m3/s
Although the effective leakage area is known, there are other leaks we are not aware of,
To account for these leaks, Q is increased by 50%, hence:
| Q1 | = | 0.8648 | m3/s
2. Air volume required when doors are opened :
| Door Area | = | 1.89 | m2
| Velocity across Door | = | 1 | m/s
| No. of Door Open considered | = | 3
| Q2 | = | Velocity across door x Door Area x No. of Door Open
| Q2 | = | 5.67 | m3/s
3. Total Air Supplied by the fan :
| Q | = | Q1 + Q2
|  | = | 6.5348 | m3/s
|  | = | 23525.2744 | m3/h
|  | = | 6534.7985 | L/s
| Q | = | 13846.455 | CFM
| at 1500 fpm | → | f = | 0.1 | "/100 ft
| Duct Length | = | 40 | m
| Friction Loss through duct | = | (Duct Length x 1.25 x 3.28 x f)
| Friction Loss | = | 0.164 | "
| Total Static Pressure | = | (PD at Register + Friction Loss + Volume Damper)*30%
|  | = | 0.2 | + | 0.164 | + | 0.2
|  | = | 0.7332 | "
|  | = | 183.3 | Pa
| Total Static Pressure on Fan | = | 183.3 | + | 15
| Total Fan Static Pressure | = | 198.3 | Pa = | 0.7932 | "
4. Relief Damper Sizing :
| Air to be releived, Q2 | = | 5.67 | m3/s
| Area of Pressure Relief, A | = | 5.67
|  |  | 0.827 | x | 15
| A | = | 1.7702 | m2
½